## DataSpan Costs
Wayne State University - C&IT Server Enclosure Bid - Schedule A | Met or Exceeded |  |  |  |  | Notes - per clarifications on Addendum 1
The minimum enclosure dimensions will be as follows:
Height- 88.9 inches (2258 mm) | N/A
Width- 29.53 inches (750mm) | N/A
Depth- 47.24 inches (1200mm) | N/A
The maximum enclosure dimensions are as follows:
Height- 91 inches (2311.4 mm) | Yes
Width- 30 inches (762mm) | Yes
Depth- 48 inches (1219.2) | Yes
Vendor is required to provide total height with castors attached within the bid package. | Yes |  |  |  |  | Provided on GL910ES-3048 drawing
Enclosures will be 48U | Yes
Enclosures will be black in color | Yes
Enclosures will meet the EIA-310-E standards for 19" server racks | Yes
Enclosure will be capable of supporting the framework for the hot aisle containment | Yes |  |  |  |  | See Containment Overview Enclosures will support Vertical Containment Panels
Enclosures will include castors and removable side panels (both sides) | Yes |  |  |  |  | Side Panels with same key locks as doors - recessed in frame
Enclosures will be provided with blanking panels in place | Yes |  |  |  |  | 48 RU in each cabinet (Installed Plenaform / Plenafill panels - removable in 1 RU increments)
Enclosures will include lockable doors, front and rear | Yes |  |  |  |  | Mesh Contour Front Door and Split Mesh Rear - Recessed in Frame with 3 hinges - 180 degree swing
90 enclosures will include standard keyed latches with a selection of 9 different keys. | Yes |  |  |  |  | Multiple key numbers will supplied for WSU to select 9 key numbers
The 45 additional latches will include a keypad lock that can be changed when needed by WSU. (Alternate options will be considered) | Yes |  |  |  |  | Mechanical CH-02 Combo lock installed - optional electronic offered - SEAL Security handles
Enclosures will be fully assembled prior to delivery | Yes |  |  |  |  | Delivered on pallets with clear protective wrapping and serial numbers
Enclosures will be provided with the bottom of the rack sealed against air flow from the cold to the hot aisle. | Yes |  |  |  |  | Solid Bottom Panel insert installed on all cabinets
All costs of delivery will be included with the bid price | Yes |  |  |  |  | Dock to Dock Delivery with 72 hour to inspect and report any for damage included
Delivery will be to the location identified by Wayne State University | Yes
Server Enclosures will be held by the vendor until delivery is requested by WSU C&IT and must be available for delivery by May 15, 2018. | Yes
|  | DataSpan | DataSpan
Item Description | QTY | Unit Cost | Total Cost | WSU Unit Cost | WSU Total
GL910ES-3048 - WSUSL Configuration - Standard key lock handles with 9 different key numbers | 90 | 2365 | 212850 | 2627.7778 | 236500 | Complete Assembled cabinets - doors, solid top, locking side panels, casters, levelers, solid bottom
GL910ES-3048 - WSUCL Configuration - Including (2) CH02 - Combo mechanical 3 (9 digit) locks for front and rear doors | 45 | 2457 | 110565 | 2730 | 122850 | Complete Assembled cabinets - doors, solid top, locking side panels, casters, levelers, solid bottom
Plenafill Blanking panels - 48RU per cabinet (Installed) | 135 | 115 | 15525 | 127.7778 | 17250
5 trucks for dock to dock delivery of 135 cabinets to Wayne State University from Edinboro Pa - Great Lakes Case and Cabinets | 1 | 6475 | 6475 |  | 6475 | Optional White Glove or inside delivery also available - (Packaging and delivery optins could provide LEED Credits)
|  |  | 345415 |  | 383075
GL-SEAL-50 - Electronic PIN Security handles with 9 digit key pad | 90 | 50 | 4500 | 55.5556 | 5000 | Upgrade to Electronic Security handle- cost for replacing 90 CH-02 mechanical handles
Please add additional lines as required.

## References Warranty
Great Lakes Data Center - References for WSU
Company | Address | Contact Name | Email | Telephone Number | Industry | Solutions Installed at location | Site Contact
Erie Insurance | 4950 W 23rd St, Erie, PA 16506 | GL - Brian Franz | brianf@greatcabinets.com | 814-881-2056 | Insurance | ES Enclosures / Cold Aisle Containment / SEAL Security | John Cox | IT Manager
American Fidelity Assurance | 9000 Cameron Pkwy. OKC Ok 73114 | GL - Ozzie Lawliss | ozziel@greatcabinets.com | 214-478-3975 | Insurance | ES Enclosures / Hot AisleContainment / InRow Cooling | Mark Morgan | IT Manager
Edinboro University | 218 Meadville St, Edinboro Pa 16444 | GL - Brian Franz | brianf@greatcabinets.com | 814-881-2056 | University | ES Enclosures / Cold Aisle Containment | TBD | IT Manager
Lord Corporation | 2455 Robison Rd EXD, Erie Pa 16509 | GL - Brian Franz | brianf@greatcabinets.com | 814-881-2056 | Manufacturing | ES Enclosures / Hot Aisle Containment | TBD | IT Manager
Lakeland Community College | 7700 Clocktower Dr. Kirtland Oh 44094 | GL - Scott Ware | sware@greatcabinets.com | 814-490-1412 | University | ES Enclosures / Cold Aisle Containment | TBD | IT Manager
These accounts were chosen based upon
similar type of applications and products
required by the customer.
GLCC Regional Manager will contact and
call to introduce each site for WSU.
ENCLOSURE WARRANTY
Great Lakes Case & Cabinet Co., Inc. warrants that each of its standard products is free from defects in material and workmanship for a period of one year from date of shipment. If within that period of time, goods shall be determined defective, these goods should be replaced or repaired at Great Lakes’ option. Under no circumstances, however, will Great Lakes be held responsible for any amount beyond the price of the product or any unauthorized “field” repair. Such correction or replacement of defective goods shall constitute a fulfillment of all liabilities in respect to such goods.